## Parameters
No. | Module | Parameter | DisplayType | Description | FunctionCode | StartAddress | DataType | Reg_Bits | Reg_BitsNum | Scalefac | Scaleoff | Endian | Unit | Comment
|  | CustomPower | num | [9 empty] | kW
|  | CustomEnergy | num | [9 empty] | kWh
|  | CustomHB | num | [9 empty] | NA
1 | DI0 | CB06_CloseStatus | num | CB06常闭节点 |  |  | Bool |  |  | 1 | 0
2 | DI1 | CB06_OpenStatus | num | CB06常开节点 |  |  | Bool |  |  | 1 | 0
3 | 1_AI0 | PCS11_UAB | line | PCS11_UAB |  |  | DBL |  |  | 0.01 | 0 |  |  | 电压信号箱1000V/10V
4 | 1_AI1 | PCS11_UBC | line | PCS11_UBC |  |  | DBL |  |  | 0.01 | 0
5 | 1_AI2 | PCS11_UCA | line | PCS11_UCA |  |  | DBL |  |  | 0.01 | 0
6 | 1_AI3 | PCS21_UAB | line | PCS21_UAB |  |  | DBL |  |  | 0.01 | 0
7 | 1_AI4 | PCS21_UBC | line | PCS21_UBC |  |  | DBL |  |  | 0.01 | 0
8 | 1_AI5 | PCS21_UCA | line | PCS21_UCA |  |  | DBL |  |  | 0.01 | 0
9 | 1_AI6 | PCS31_UAB | line | PCS31_UAB |  |  | DBL |  |  | 0.01 | 0
10 | 1_AI7 | PCS31_UBC | line | PCS31_UBC |  |  | DBL |  |  | 0.01 | 0
11 | 1_AI8 | PCS31_UCA | line | PCS31_UCA |  |  | DBL |  |  | 0.01 | 0
12 | 1_AI9 | PCS11_UDC | line | PCS11_UDC |  |  | DBL |  |  | 0.01 | 0
13 | 1_AI10 | PCS21_UDC | line | PCS21_UDC |  |  | DBL |  |  | 0.01 | 0
14 | 1_AI11 | PCS31_UDC | line | PCS31_UDC |  |  | DBL |  |  | 0.01 | 0
15 | 2_AI0 | PCS11_IA | line | PCS11_IA |  |  | DBL |  |  | 0.05 | 0 |  |  | 电流信号箱200A/10V
16 | 2_AI1 | PCS11_IB | line | PCS11_IB |  |  | DBL |  |  | 0.05 | 0
17 | 2_AI2 | PCS11_IC | line | PCS11_IC |  |  | DBL |  |  | 0.05 | 0
18 | 2_AI3 | PCS21_IA | line | PCS21_IA |  |  | DBL |  |  | 0.05 | 0
19 | 2_AI4 | PCS21_IB | line | PCS21_IB |  |  | DBL |  |  | 0.05 | 0
20 | 2_AI5 | PCS21_IC | line | PCS21_IC |  |  | DBL |  |  | 0.05 | 0
21 | 2_AI6 | PCS31_IA | line | PCS31_IA |  |  | DBL |  |  | 0.05 | 0
22 | 2_AI7 | PCS31_IB | line | PCS31_IB |  |  | DBL |  |  | 0.05 | 0
23 | 2_AI8 | PCS31_IC | line | PCS31_IC |  |  | DBL |  |  | 0.05 | 0
24 | 2_AI9 | PCS21_IDC | line | PCS21_IDC |  |  | DBL |  |  | 0.05 | 0
25 | 2_AI10 | PCS11_IDC | line | PCS11_IDC |  |  | DBL |  |  | 0.05 | 0
26 | 2_AI11 | PCS31_IDC | line | PCS31_IDC |  |  | DBL |  |  | 0.05 | 0
27 | Model_Input | pswagc | num | 输入-AGC指令输入 |  |  | DBL |  |  | 1 | 0
28 | Model_Input | pswgenerator | num | 输入-发电机功率 |  |  | DBL |  |  | 1 | 0
29 | Model_Input | K1 | num | 输入-K1 |  |  | DBL |  |  | 1 | 0
30 | Model_Input | K3 | num | 输入-K3 |  |  | DBL |  |  | 1 | 0
31 | Model_Input | K2 | num | 输入-K2 |  |  | DBL |  |  | 1 | 0
32 | Model_Input | Step | num | 输入-执行步长 |  |  | DBL |  |  | 1 | 0
33 | Model_Output | power | num | 输出-辅助调频功率 |  |  | DBL |  |  | 1 | 0
34 | Model_Output | pswagc out | num | 输出 |  |  | DBL |  |  | 1 | 0
35 | Model_Output | pswgenerator out | num | 输出 |  |  | DBL |  |  | 1 | 0
36 | Model_Output | K1_out | num | 输出 |  |  | DBL |  |  | 1 | 0
37 | Model_Output | K2_out1 | num | 输出 |  |  | DBL |  |  | 1 | 0
38 | Model_Output | K3_out2 | num | 输出 |  |  | DBL |  |  | 1 | 0
39 | Model_Output | powerSum | num | 输出-辅助调频能量输出 |  |  | DBL |  |  | 1 | 0
40 | System | ModelRunFlag | num | 模型运行标志 |  |  | DBL |  |  | 1 | 0
41 | System | PCSRunFlag | num | PCS运行标志 |  |  | DBL |  |  | 1 | 0
42 | PCS | PCS100_invertermode | num | Present operating mode of the Virtual generator: 0: Inhibited 1: Stopped 2: Run 9: Undefined status | 0x03 | 400010 | DBL |  |  | 1 | 0
43 | PCS | PCS100_Overallstatus | num | Alarm and operating status of the Virtual generator as a single enumerated register. 0: No Alarms 1: Warning 2: Fault | 0x03 | 400011 | DBL |  |  | 1 | 0
44 | PCS | PCS100_Maxtemp | num | Maximum temperature measured in any part of the Virtual generator system | 0x03 | 400012 | DBL |  |  | 0.1 | 0
45 | PCS | PCS100_Dcvoltage | num | Measured voltage on the DC input to the Virtual generator | 0x03 | 400013 | DBL |  |  | 0.1 | 0
46 | PCS | PCS100_DC Breaker | num | DC contactor is closed/open. | 0x03 | 400014:0 | Bool |  |  | 1 | 0
47 | PCS | PCS100_AC Breaker | num | AC contactor is closed/open | 0x03 | 400014:1 | Bool |  |  | 1 | 0
48 | PCS | Heartbeat | num | Heartbeat from inverter | 0x03 | 400014:6 | Bool |  |  | 1 | 0
49 | PCS | PCS100_Acvoltage | line | Output average voltage (rms) for Virtual generator system | 0x03 | 400015 | DBL |  |  | 0.1 | 0
50 | PCS | PCS100_Accurrent | line | Output average current (rms) for Virtual generator system | 0x03 | 400016 | DBL |  |  | 0.1 | 0
51 | PCS | PCS100_realpoweroutput | line | The measured real power output from the for Virtual generator system. kW < 0: power drawn from the grid kW > 0: power into the grid | 0x03 | 400017 | DBL |  |  | 0.1 | 0
52 | PCS | PCS100_reactivepoweroutput | line | The measured reactive power output from the for Virtual generator system. kVAr < 0: Inductive Power kVAr > 0: Capacitive Power | 0x03 | 400018 | DBL |  |  | 0.1 | 0
53 | PCS | PCS100_apparentpoweroutput | line | The measured apparent power output from the for Virtual generator system. | 0x03 | 400019 | DBL |  |  | 0.1 | 0
54 | PCS | PCS100_VoltagephaseA | line | Phase A voltage for Virtual generator system | 0x03 | 400020 | DBL |  |  | 0.1 | 0
55 | PCS | PCS100_VoltagephaseB | line | Phase B voltage for Virtual generator system | 0x03 | 400021 | DBL |  |  | 0.1 | 0
56 | PCS | Pcs100_VoltagephaseC | line | Phase C voltage for Virtual generator system | 0x03 | 400022 | DBL |  |  | 0.1 | 0
57 | PCS | Pcs100_CurrentlinA | line | Phase A current for Virtual generator system | 0x03 | 400023 | DBL |  |  | 0.1 | 0
58 | PCS | Pcs100_CurrentlinB | line | Phase B current for Virtual generator system | 0x03 | 400024 | DBL |  |  | 0.1 | 0
59 | PCS | Pcs100_CurrentlinC | line | Phase C current for Virtual generator system | 0x03 | 400025 | DBL |  |  | 0.1 | 0
60 | PCS | Pcs100_Powerfactor | num | Scale 100 for Virtual generator system | 0x03 | 400026 | DBL |  |  | 0.01 | 0
61 | PCS | Pcs100_Frequency | num | for Virtual generator system | 0x03 | 400027 | DBL |  |  | 0.1 | 0
62 | PCS | ESI_Invertermode | num | Present operating mode of the ESI: 1: Stopped 2: Run 9: Undefined status | 0x03 | 400101 | DBL |  |  | 1 | 0
63 | PCS | ESI_Overallstatus | num | Alarm and operating status of the ESI as a single enumerated register. 0: No Alarms 1: Warning 2: Fault | 0x03 | 400102 | DBL |  |  | 1 | 0
64 | PCS | ESI_Air_Temp | num | Maximum temperature measured in any part of the Virtual generator system | 0x03 | 400103 | DBL |  |  | 0.1 | 0
65 | PCS | ESI_Dcvoltage | num | Measured voltage on the DC input to the Virtual generator | 0x03 | 400104 | DBL |  |  | 0.1 | 0
66 | PCS | ESI_DC Breaker | num | DC contactor is closed/open. | 0x03 | 400105 | DBL |  |  | 1 | 0
67 | PCS | ESI_AC Breaker | num | AC contactor is closed/open | 0x03 | 400106 | DBL |  |  | 1 | 0
68 | PCS | ESI_Acvoltage | line | Output average voltage (rms) for ESI | 0x03 | 400107 | DBL |  |  | 0.1 | 0
69 | PCS | ESI_Accurrent | line | Output average current (rms) for ESI | 0x03 | 400108 | DBL |  |  | 0.1 | 0
70 | PCS | ESI_realpoweroutput | line | The measured real power output from the for ESI. kW < 0: power drawn from the grid kW > 0: power into the grid | 0x03 | 400109 | DBL |  |  | 0.1 | 0
71 | PCS | ESI_reactivepoweroutput | line | The measured reactive power output from the for ESI kVAr < 0: Inductive Power kVAr > 0: Capacitive Power | 0x03 | 400110 | DBL |  |  | 0.1 | 0
72 | PCS | ESI_apparentpoweroutput | line | The measured apparent power output from the for ESI | 0x03 | 400111 | DBL |  |  | 0.1 | 0
73 | PCS | ESI_Powerfactor | num | Scale 100 for ESI | 0x03 | 400112 | DBL |  |  | 0.01 | 0
74 | PCS | ESI_Frequency | num | for ESI | 0x03 | 400113 | DBL |  |  | 0.1 | 0
75 | PCS | ISU_Invertermode | num | Present operating mode of the ISU: 1: Stopped 2: Run 9: Undefined status | 0x03 | 400201 | DBL |  |  | 1 | 0
76 | PCS | ISU_Overallstatus | num | Alarm and operating status of the ISU as a single enumerated register. 0: No Alarms 1: Warning 2: Fault | 0x03 | 400202 | DBL |  |  | 1 | 0
77 | PCS | ISU_Acvoltage | line | Output average voltage (rms) for ISU | 0x03 | 400203 | DBL |  |  | 0.1 | 0
78 | PCS | ISU_Accurrent | line | Output average current (rms) for ISU | 0x03 | 400204 | DBL |  |  | 0.1 | 0
79 | PCS | ISU_realpoweroutput | line | The measured real power output from the for ISU. kW < 0: power drawn from the grid kW > 0: power into the grid | 0x03 | 400205 | DBL |  |  | 0.1 | 0
80 | PCS | ISU_reactivepoweroutput | line | The measured reactive power output from the for ISU kVAr < 0: Inductive Power kVAr > 0: Capacitive Power | 0x03 | 400206 | DBL |  |  | 0.1 | 0
81 | PCS | ISU_apparentpoweroutput | line | The measured apparent power output from the for ISU | 0x03 | 400207 | DBL |  |  | 0.1 | 0
82 | PCS | ISU_DC_Voltage | num | The DC voltage of ISU | 0x03 | 400208 | DBL |  |  | 0.1 | 0
83 | PCS | CB_Status_CB01_Closed | num | CB01_Closed: 1= Closed ,0=Opened | 0x03 | 400209:0 | Bool |  |  | 1 | 0
84 | PCS | CB_Status_CB02_Closed | num | CB02_Closed: 1= Closed ,0=Opened | 0x03 | 400209:1 | Bool |  |  | 1 | 0
85 | PCS | CB_Status_CB03_Closed | num | CB03_Closed: 1= Closed ,0=Opened | 0x03 | 400209:2 | Bool |  |  | 1 | 0
86 | PCS | CB_Status_CB04_Closed | num | CB04_Closed: 1= Closed ,0=Opened | 0x03 | 400209:3 | Bool |  |  | 1 | 0
87 | PCS | CB_Status_CB05_Closed | num | CB05_Closed: 1= Closed ,0=Opened | 0x03 | 400209:4 | Bool |  |  | 1 | 0
88 | PCS | CB_Status_CB12_Closed | num | CB12_Closed: 1= Closed ,0=Opened | 0x03 | 400209:5 | Bool |  |  | 1 | 0
89 | PCS | CB_Status_CB21_Closed | num | CB21_Closed: 1= Closed ,0=Opened | 0x03 | 400209:6 | Bool |  |  | 1 | 0
90 | PCS | CB_Status_CB22_Closed | num | CB22_Closed: 1= Closed ,0=Opened | 0x03 | 400209:7 | Bool |  |  | 1 | 0
91 | PCS | CB_Status_CB32_Closed | num | CB32_Closed: 1= Closed ,0=Opened | 0x03 | 400209:8 | Bool |  |  | 1 | 0
92 | PCS | CB12_Close_Command | num | CB12_Close_Command: 1:=Close | 0x03 | 400210:0 | Bool |  |  | 1 | 0
93 | PCS | CB12_Open_Command | num | CB12_Open_Command: 1:=Open | 0x03 | 400210:1 | Bool |  |  | 1 | 0
94 | PCS | CB05_Close_Command | num | CB05_Close_Command: 1:=Close | 0x03 | 400210:2 | Bool |  |  | 1 | 0
95 | PCS | CB05_Open_Command | num | CB05_Open_Command: 1:=Open | 0x03 | 400210:3 | Bool |  |  | 1 | 0
96 | PCS | CB06_Close_Command | num | CB06_Close_Command: 1:=Close | 0x03 | 400210:4 | Bool |  |  | 1 | 0
97 | PCS | CB06_Open_Command | num | CB06_Open_Command: 1:=Open | 0x03 | 400210:5 | Bool |  |  | 1 | 0
98 | PCS | CB22_Close_Command | num | CB22_Close_Command: 1:=Close | 0x03 | 400210:6 | Bool |  |  | 1 | 0
99 | PCS | CB22_Open_Command | num | CB22_Open_Command: 1:=Open | 0x03 | 400210:7 | Bool |  |  | 1 | 0
100 | PCS | CB32_Close_Command | num | CB32_Close_Command: 1:=Close | 0x03 | 400210:8 | Bool |  |  | 1 | 0

## ReadConfig
FunctionCode | StartAddress | Amount | Timeout
0x03 | 400010 | 18 | 100
0x03 | 400101 | 13 | 100
0x03 | 400201 | 10 | 100

## WriteConfig
No. | Module | Parameter | Description | FunctionCode | StartAddress | DataType | Comment | DefaultValue
1 | PCS | PCS100_Realdemand |  | 0x06 | 400501 | U16 | Kw command issued to .Virtual generator
2 | PCS | PCS100_Reactivedemand |  | 0x06 | 400502 | U16 | Kvar command issued to Virtual generator.
3 | PCS | PCS100_Shutdown |  | 0x06 | 400503:0 | Bool | Stop the Virtual generator.0:=stop;
4 | PCS | PCS100_Run |  | 0x06 | 400503:1 | Bool | Run the Virtual generator.1:=run;
5 | PCS | PCS100_Reset |  | 0x06 | 400503:2 | Bool | Reset the Virtual Generator.1:=reset,0:=no reset
6 | PCS | Watchdog |  | 0x06 | 400503:3 | Bool | Write the bit to toggle the heartbeat.
7 | PCS | PCS100_DC_Voltage_Ref |  | 0x06 | 400504 | U16 | The DC voltage reference of PCS100
8 | PCS | ESI_Realdemand |  | 0x06 | 400511 | I16 | Kw command issued to ESI
9 | PCS | ESI_Reactivedemand |  | 0x06 | 400512 | I16 | Kvar command issued to ESI.
10 | PCS | ESI_Shutdown |  | 0x06 | 400513:0 | Bool | Stop the ESI.0:=stop;
11 | PCS | ESI_Run |  | 0x06 | 400513:1 | Bool | Run the ESI.1:=run;
12 | PCS | ESI_Reset |  | 0x06 | 400513:2 | Bool | Reset the ESI.1:=reset,0:=no reset
13 | PCS | ESI_DC_Voltage_Ref |  | 0x06 | 400514 | U16 | The DC voltage reference of ESI
14 | PCS | ISU_Shutdown |  | 0x06 | 400521:0 | Bool | Stop the ISU.0:=stop;
15 | PCS | ISU_Run |  | 0x06 | 400521:1 | Bool | Run the ISU.1:=run;
16 | PCS | ISU_Reset |  | 0x06 | 400521:2 | Bool | Reset the ISU.1:=reset,0:=no reset
17 | PCS | ISU DCVoltage Ref |  | 0x06 | 400522 | U16 | DC Voltage Reference
18 | PCS | ISU_Realdemand |  | 0x06 | 400523 | I16 | Kw command issued to ISU
19 | PCS | ISU_Reactivedemand |  | 0x06 | 400524 | I16 | Kvar command issued to ISU
20 | PCS | ISU mode change |  | 0x06 | 400525:0 | Bool | ISU mode change 1:=DC control,0=Power
21 | PCS | PCS mode change |  | 0x06 | 400525:1 | Bool | PCS mode change 1:=DCcontrol,0=Power
22 | PCS | ESI mode change |  | 0x06 | 400525:2 | Bool | ESI mode change 1:=DC control,0=Power
23 | PCS | CB21_Close_Command |  | 0x06 | 400526:0 | Bool | CB21_Close_Command: 1:=Close
24 | PCS | CB21_Open_Command |  | 0x06 | 400526:1 | Bool | CB21_Open_Command: 1:=Open
25 | PCS | CB22_Close_Command |  | 0x06 | 400526:2 | Bool | CB22_Close_Command: 1:=Close
26 | PCS | CB22_Open_Command |  | 0x06 | 400526:3 | Bool | CB22_Open_Command: 1:=Open
27 | PCS | CB32_Close_Command |  | 0x06 | 400526:4 | Bool | CB32_Close_Command: :1=Close,0:=Open
28 | PCS | CB06_Status |  | 0x06 | 400527:0 | Bool | CB06_Closed 1:=Closed,0:=Opened
29 | Switch | CB12_Close | DO0 |  |  | Bool | CB12合
30 | Switch | CB12_Open | DO1 |  |  | Bool | CB12分
31 | Switch | CB05_Close | DO2 |  |  | Bool | CB05合
32 | Switch | CB05_Open | DO3 |  |  | Bool | CB05分
33 | Switch | CB06_Close | DO4 |  |  | Bool | CB06合
34 | Switch | CB06_Open | DO5 |  |  | Bool | CB06分

## 设备逻辑参数列表
No. | Module | Parameter | Description | DataTag | DataFrom/To | Comment
1 | Model | Model_Load | 加载模型 | Model_Load | UI
2 | Model | Model_Start | 模型开始 | Model_Start | UI
3 | Model | Model_Stop | 模型停止 | Model_Stop | UI
4 | Model | Model_Pause | 模型暂停 | Model_Pause | UI
5 | Model | Model_Resume | 模型重新开始 | Model_Resume | UI
6 | Model | K1 | 比例系数K1 | K1 | UI
7 | Model | K2 | 比例系数K2 | K2 | UI
8 | Model | K3 | 比例系数K3 | K3 | UI
9 | PCS | PCS_Start | 调频系统开始运行 | PCS_Start | UI
10 | PCS | PCS_Stop | 调频系统停止运行 | PCS_Stop | UI
11 | UI | Start_Stop |  |  |  | Start 1 Stop 0 Restart 2
12 | UI | K1
13 | UI | K2
14 | UI | K3